## Sheet1
Orient Road Jail
|  | 2 1/2" Hose Valve Listing | 2 1/2 Pressure Reducing Hose Valve
108 Total Valves
NFPA 25 13.5.2.2 Test – May 2017
Valve No. | Size | Type | Location | Building | Floor | Pressure @ Valve | Pitot 1 1/8" | GPM | Comments
1 | 2 1/2" | Pressure Reducing | End of 12 Tunnel Stairs | 12 | Second | 150/4 |  |  | 300 ft of hose
2 | 2 1/2" | Pressure Reducing | Building 7 - Tunnel | 7 | Third | 145
3 | 2 1/2" | Pressure Reducing | Building 8 - Tunnel | 8 | Third | 150/4
4 | 2 1/2" | Pressure Reducing | Building 6 - Tunnel | 6 | Third | 125/5
5 | 2 1/2" | Pressure Reducing | South Cmd Apex-Tunnel | 8 | Third | 150/6
6 | 2 1/2" | Pressure Reducing | Building 5 - Tunnel | 5 | Third | 150/4
7 | 2 1/2" | Pressure Reducing | Building 4 - Tunnel | 4 | Third | 150/5
8 | 2 1/2" | Pressure Reducing | Building 1 - Tunnel | 1 | Third | 145/25
9 | 2 1/2" | Pressure Reducing | North Cmd Apex-Tunnel | 11 | Third | 140
10 | 2 1/2" | Pressure Reducing | Building 2 - Tunnel | 2 | Third | 145/15
11 | 2 1/2" | Pressure Reducing | Building 3 - Tunnel | 3 | Third | 145/20
12 | 2 1/2" | Pressure Reducing | Building 11 - Tunnel | 11 | Third | 155/20
13 | 2 1/2" | Pressure Reducing | Tunnel Entrance | 13 | Second | 125/10
14 | 2 1/2" | Pressure Reducing | 7 Alpha Stairwell | 7 | Second | 125
15 | 2 1/2" | Pressure Reducing | Bldg 11 Stairwell | 11 | Second | 145/20
16 | 2 1/2" | Pressure Reducing | North Command Apex | 11 | Second | 150
17 | 2 1/2" | Pressure Reducing | HU 1 Stairwell A&B | 1 | Second | 145
18 | 2 1/2" | Pressure Reducing | HU 2 Stairwell A&B | 2 | Second | 140
19 | 2 1/2" | Pressure Reducing | HU 3 Stairwell C&D | 3 | Second | 145
20 | 2 1/2" | Pressure Reducing | 7B Stairwell | 7 | Second | 125
21 | 2 1/2" | Pressure Reducing | Front Lobby Stairwell | 11 | Second | 150
22 | 2 1/2" | Pressure Reducing | 7D Stairwell | 8 | Second | 125
23 | 2 1/2" | Pressure Reducing | South Command Apex | 8 | Second | 130
24 | 2 1/2" | Pressure Reducing | HU 4 Stairwell A&B | 4 | Second | 130
25 | 2 1/2" | Pressure Reducing | HU 5 Stairwell C&D | 5 | Second | 130
26 | 2 1/2" | Pressure Reducing | HU 6 Stairwell A&B | 6 | Second |  |  |  | valve needs to be turned
27 | 2 1/2" | Pressure Reducing | Bldg 9 Employee Entrance | 9 | First | 150/6 |  |  | Need SKD 25
28 | 2 1/2" | Pressure Reducing | South Command Apex | 8 | First | 145
29 | 2 1/2" | Pressure Reducing | Bldg 8 Clinic | 8 | First | 140
30 | 2 1/2" | Pressure Reducing | 7 Delta Stairwell | 8 | First |  |  |  | valve needs to be turned
31 | 2 1/2" | Pressure Reducing | Pod 7 Delta | 8 | First | 135
32 | 2 1/2" | Pressure Reducing | 7 Bravo Stairwell | 7 | First |  |  |  | valve needs to be turned
33 | 2 1/2" | Pressure Reducing | Pod 7 Bravo | 7 | First | 130
34 | 2 1/2" | Pressure Reducing | 7 Charlie Vestibule | 7 | First | 140
35 | 2 1/2" | Pressure Reducing | Pod 7 Alpha | 7 | First | 140
36 | 2 1/2" | Pressure Reducing | 7 Alpha Stairwell | 7 | First | 140
37 | 2 1/2" | Pressure Reducing | Bldg 10 Central Booking | 10 | First | 135
38 | 2 1/2" | Pressure Reducing | Booking Sgt Office | 10 | First | 130
39 | 2 1/2" | Pressure Reducing | Front Lobby | 11 | First | 130
40 | 2 1/2" | Pressure Reducing | Admin DMB Office | 11 | First | 130
41 | 2 1/2" | Pressure Reducing | Admn Commanders Hallway | 11 | First | 130
42 | 2 1/2" | Pressure Reducing | Bldg 11 Stairwell | 11 | First | 145
43 | 2 1/2" | Pressure Reducing | Staff Dining | 12 | First | 140
44 | 2 1/2" | Pressure Reducing | Bldg 12 Hallway | 12 | First | 140
45 | 2 1/2" | Pressure Reducing | Bldg 13 Engineering | 13 | First | 130
46 | 2 1/2" | Pressure Reducing | North Command Apex | 11 | First | 140
47 | 2 1/2" | Pressure Reducing | HU 1 Stairwell A&B | 1 | First | 145
48 | 2 1/2" | Pressure Reducing | Pod 1 Alpha | 1 | First | 145/10
49 | 2 1/2" | Pressure Reducing | Pod 1 Bravo | 1 | First | 150/15
50 | 2 1/2" | Pressure Reducing | 1 C Tower Stairwell ST01 | 1 | First | 145
51 | 2 1/2" | Pressure Reducing | 1 C Tower Stairwell ST01 | 1 | Second | 145
52 | 2 1/2" | Pressure Reducing | 1 Charlie Pantry | 1 | First | 145
53 | 2 1/2" | Pressure Reducing | Pod 1 Delta | 1 | First | 150/15
54 | 2 1/2" | Pressure Reducing | HU 2 Stairwell A&B | 2 | First | 150
55 | 2 1/2" | Pressure Reducing | Pod 2 Alpha | 2 | First | 150
56 | 2 1/2" | Pressure Reducing | Pod 2 Bravo | 2 | First | 155 |  |  | Hard to Turn
57 | 2 1/2" | Pressure Reducing | Pod 2 Charlie | 2 | First | 155
58 | 2 1/2" | Pressure Reducing | Pod 2 Delta | 2 | First | 145
59 | 2 1/2" | Pressure Reducing | HU 3 Stairwell C&D | 3 | First | 150
60 | 2 1/2" | Pressure Reducing | Pod 3 Alpha | 3 | First | 145 |  |  | Stop Bent
61 | 2 1/2" | Pressure Reducing | Pod 3 Bravo | 3 | First | 155
62 | 2 1/2" | Pressure Reducing | Pod 3 Charlie | 3 | First | 145
63 | 2 1/2" | Pressure Reducing | Pod 3 Delta | 3 | First | 145
64 | 2 1/2" | Pressure Reducing | HU 4 Stairwell A&B | 4 | First | 135
65 | 2 1/2" | Pressure Reducing | Pod 4 Alpha | 4 | First | 150
66 | 2 1/2" | Pressure Reducing | Pod 4 Bravo | 4 | First | 150
67 | 2 1/2" | Pressure Reducing | Pod 4 Charlie | 4 | First | 150
68 | 2 1/2" | Pressure Reducing | Pod 4 Delta | 4 | First | 140
69 | 2 1/2" | Pressure Reducing | HU 5 Stairwell C&D | 5 | First | 135
70 | 2 1/2" | Pressure Reducing | Pod 5 Alpha | 5 | First | 145
71 | 2 1/2" | Pressure Reducing | Pod 5 Bravo | 5 | First | 145
72 | 2 1/2" | Pressure Reducing | Pod 5 Charlie | 5 | First | 145
73 | 2 1/2" | Pressure Reducing | Pod 5 Delta | 5 | First | 145
74 | 2 1/2" | Pressure Reducing | HU 6 Stairwell A&B | 6 | First | 135
75 | 2 1/2" | Pressure Reducing | Pod 6 Alpha | 6 | First | 140
76 | 2 1/2" | Pressure Reducing | Pod 6 Bravo | 6 | First | 145
77 | 2 1/2" | Pressure Reducing | 6C Tower Stairwell ST01 | 6 | First | 145
78 | 2 1/2" | Pressure Reducing | 6C Tower Stairwell ST01 | 6 | Second | 140
79 | 2 1/2" | Pressure Reducing | 6 Charlie Pantry | 6 | First | 140
80 | 2 1/2" | Pressure Reducing | Pod 6 Delta | 6 | First | 140
Valve No. | Size | Type | Location | Building | Floor | Static | Residual | Pitot 2 1/2 | GPM | Residual
81 | 2 1/2" | Standard Angle Valve | Warehouse - South | 14 | First
82 | 2 1/2" | Standard Angle Valve | Warehouse - North | 14 | First
83 | 2 1/2" | Standard Angle Valve | Bldg 9 Mechanical Room | 9 | Second | 150/20
84 | 2 1/2" | Roof Manifold "Y" valve | Engineering- Roof Hatch | 13 | Roof | 150/15
85 | 2 1/2" | Roof Manifold "Y" valve | Kitchen- Roof South | 12 | Roof | 150/10
86 | 2 1/2" | Roof Manifold "Y" valve | Kitchen -Roof North | 12 | Roof | 150/15
87 | 2 1/2" | Roof Manifold "Y" valve | Administration - North | 11 | Roof | 150/24 |  |  |  | 15
88 | 2 1/2" | Roof Manifold "Y" valve | Administration - East | 11 | Roof | 145/15
89 | 2 1/2" | Roof Manifold "Y" valve | Booking -North | 10 | Roof | 150/25 |  |  | Outlet Hrzt | 85
90 | 2 1/2" | Roof Manifold "Y" valve | Booking - South | 10 | Roof | 150/25 |  |  |  | 90
91 | 2 1/2" | Roof Manifold "Y" valve | Employee Entrance - East | 9 | Roof | 150/32 |  |  |  | 79
92 | 2 1/2" | Roof Manifold "Y" valve | Employee Entrance - West | 9 | Roof | 125/30 |  |  |  | 83
93 | 2 1/2" | Roof Manifold "Y" valve | 7 Delta - East | 8 | Roof | 150/20 |  |  |  | 120
94 | 2 1/2" | Roof Manifold "Y" valve | 7 Delta - West | 8 | Roof | 145/20 |  |  |  | 91
95 | 2 1/2" | Roof Manifold "Y" valve | Pod 7A -North | 7 | Roof | 145/20 |  |  |  | 90
96 | 2 1/2" | Roof Manifold "Y" valve | Pod 7B -South | 7 | Roof | 150/15
97 | 2 1/2" | Roof Manifold "Y" valve | Building 6 (A&B) | 6 | Roof | 145/20 |  |  |  | 79
98 | 2 1/2" | Roof Manifold "Y" valve | Building 6 (C&D) | 6 | Roof | 150/15 |  |  |  | 76
99 | 2 1/2" | Roof Manifold "Y" valve | Building 5 (A&B) | 5 | Roof | 150/20 |  |  |  | 76
100 | 2 1/2" | Roof Manifold "Y" valve | Building 5 (C&D) | 5 | Roof | 150/20 |  |  |  | 79
101 | 2 1/2" | Roof Manifold "Y" valve | Building 4 (A&B) | 4 | Roof | 150/15 |  |  | Outlet Hrzt | 79
102 | 2 1/2" | Roof Manifold "Y" valve | Building 4 (C&D) | 4 | Roof | 150/na |  |  | Outlet Hrzt | 94
103 | 2 1/2" | Roof Manifold "Y" valve | Building 3 (A&B) | 3 | Roof | 145/20 |  |  |  | 80
104 | 2 1/2" | Roof Manifold "Y" valve | Building 3 (C&D) | 3 | Roof | 145/20 |  |  |  | 85
105 | 2 1/2" | Roof Manifold "Y" valve | Building 2 (A&B) | 2 | Roof | 150/15 |  |  |  | 75
106 | 2 1/2" | Roof Manifold "Y" valve | Building 2 (C&D) | 2 | Roof | 150/20 |  |  |  | 86
107 | 2 1/2" | Roof Manifold "Y" valve | Building 1 (A&B) | 1 | Roof | 150/15 |  |  |  | 95
108 | 2 1/2" | Roof Manifold "Y" valve | Building 1 (C&D) | 1 | Roof | 145/20 |  |  |  | 65
*7 Delta is located in Building #8
First Floor | 54
Second Floor | 17
Third Floor | 12
Roof | 25
TOTAL | 108

## Sheet2
Static Residual | Static | Pitot 1 1/2 | GPM
156
120
120
156
120
167
156
163
163
100
150
150
159
157
157
160
159
159
155
160
154
156
160
156