ORJ Kitchen Hood Suppression Systems (NFPA 17) 9-3.1

Inspected and alarm tested twice a year

11-14-17

Hoods were last cleaned by Hoodmasters 01-20-17

11.2.4 Fusible links (including fusible links on fire damper

assemblies) and automatic sprinkler heads shall be replaced at

least annually, or more frequently if necessary where required

by the manufacturer.

11.2.5 The year of manufacture and the date of installation of

the fusible links shall be marked on the system inspection tag.

The tag shall be signed or initialed by the installer.

ANSUL SYSTEM over fryer and grill – Has 9 fusible links (2 are in the ducts and 1 is over the two large mixers) and three, 3 gallon tanks, 2 are located in  OF-04  and 1 is located in CF-01. Pullstation relocated 04/29/13.

*Links are 450 degree “A-PC”

Gas will reset when the fire alarm is reset – Ensure that the pilot lights are re-ignited

Link over mixers in behind pull out panels, not access panel

Must test system with fire alarm in normal mode – Do not bypass

**Will need a drill with a 1/4 bit driver to remove access panel screws quickly**

RANGEGAURD SYSTEM over large kettles – Has 4 fusible links and 3 tanks, one 4 gallon tank and two 2- .66 gallon tanks which are located in OF-04-01. Installed 2003 - Must re-insert pull pin before head will reset.

*Links are 360 degree “ML”

When the RANGEMASTER system is activated, the breakers for the kettles also need to be reset. These are located in ME-01 at the end of the BLD 12 tunnel. Kettles are electric.

**GAS DOES NOT SHUT DOWN WITH ACTIVATION OF THIS SYSTEM**

**Will need 8 foot ladder to access links above the kettles and a Allen Key set to remove Anusl Pullstation bar. Contractor needs a “cocking lever” and a lock bar to properly test the system

POST TESTING – ENSURE ALL OF THE FOLLOWING HAPPENS:

ALL nitrogen cartridges have been reinstalled - Don't forget the one in Ms. Hayes' Office.

Gas is back on

Pilot lights are re-ignited

All old links are removed from the facility by the contractor

Old nitrogen cartridges have been removed by the contractor