ORIENT ROAD JAIL

Wet/Dry Suppression System Testing Information

Updated 04/06/2020

*TURN OFF FIRE PUMP (FP- 00) BEFORE TESTING ANYTHING!

Bring side cutters, channel lock pliers, crescent wrenches, valve knob tool and LPS 1

Sign out a set of the facility emergency keys (Set 22 in OSC)

70 Total Risers

(69 wet and 1 dry pipe)

Quarterly Testing Requirements per NFPA 25

Wet Systems

Hydraulic Calculation plates in place (ORJ has never had any)

Inspect:

All FDC connections

All valves - Are in the appropriate open or closed position

Control Valves – Insure they are locked, sealed or supervised

Gauges - Indicate that normal water pressure (125-175 PSI) is being maintained

Test:

Water flow alarms – Ensure signal is received by panel in OSC

Supervisory switches on the Control Valves – Ensure signal is received by panel in OSC.

Main Drain

Pre-Action Systems

Hydraulic Calculation plates in place (ORJ has never had any)

Inspect:

All FDC connections

All valves - Are in the appropriate open or closed position

Control Valves – Insure they are locked, sealed or supervised

Gauges - Indicate that normal water pressure (125-175 PSI) and normal air pressure (50 PSI) is being maintained

Valve seats – Ensure there is no leakage

All electrical components are in service.

Test:

Water flow alarms – Ensure signal is received by panel in OSC

Supervisory switches on the Control Valves – Ensure signal is received by panel in OSC

Main Drain

Annual Sprinkler Testing Requirements (In addition to the quarterly items)

The 15 butterfly valves on the 3rd floor need to be exercised as well – will need a 24 key. There is also one in the Bld #13 locker room, Chiller room (High Up) and in ME-01 at the end of the tunnel.  Tag and date each year

A check of all sprinklers, hangers, pipe and fittings. Must go into every pod and area. **Keep a close eye on orientation, Sprinkler heads in HU 6A (25-48) 6B (1, 23, 28) 6C and 6D (25-48) are correct even though they look wrong, they have a deflector...Must look for the word TOP.

Perform a trip test on the dry pipe systems (1 in Bld 14) – THIS IS NOT OPTIONAL SEE NFPA 25 – 12.4.3.2.2

Other Testing Notes

Sprinkler system gauges must be replaced of calibrated every 5 years

(NFPA 25-9-2.8.2) - Last performed 2018

System check and deluge valves must be inspected internally every 5 years to verify that all operate properly components.

(NFPA 25 -9-4.2.1)

The 108 fire hose valves must be tested every 5 years

(NFPA 25-12-5.2.2) - Last performed May 2017

Dry Pendant heads are in the coolers in Building 12 and on the loading dock and coolers in Building 14. All heads were replaced in June of 2013.

NFPA 25

5.3.1.1.1.6 - Dry sprinklers that have been in service for 10 years shall be replaced or tested.

Building 1

(Housing Unit 1)

Risers are located in the Housing Unit 1 Sprinkler Room (SP- 01)

6 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 1A | Wet | On Riser & JC-02 of Pod 1A |
| B | Pod 1B | Wet | On Riser & JC-02 of Pod 1B |
| C | Pod 1C | Wet | On Riser & JC-02 of 1C Tower Hallway |
| D | Pod 1 D | Wet | On Riser & JC-02 of Pod 1D |
| E* | 1st Floor Corridor | Wet | On Riser |
| F* | 2nd Floor Corridor | Wet | On Riser |

Gas reset is automatic

Gas reset box is located in the HU 1 F.A.C.P. room (ME-01) on the 2nd floor in the visitation corridor. Alarm panel (NODE 1) is located in the same room.

While flow testing risers E and F, did each of the following happen?

1st floor hallway fire doors close    Y or N

2nd floor hallway fire doors close   Y or N

Gas cut off is automatic

* Core fan will run when water is flowed on these 2 risers

Phone in ME-02   Ext 3720

Building 2

(Housing Unit 2)

Risers are located in the Housing Unit 2 Sprinkler Room (SP- 01)

6 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 2A | Wet | On Riser & JC-02 of Pod 2A |
| B | Pod 2B | Wet | On Riser & JC-02 of Pod 2B |
| C | Pod 2C | Wet | On Riser & JC-02 of Pod 2C |
| D | Pod 2D | Wet | On Riser & JC-02 of Pod 2D |
| E* | 1st Floor Corridor | Wet | On Riser |
| F* | 2nd Floor Corridor | Wet | On Riser |

Gas reset is automatic

Gas reset box is located in the HU 2 F.A.C.P. room (ME-01) on the 2nd floor in the visitation corridor. Alarm panel (NODE 2) is located in the same room.

While flow testing risers E and F, did each of the following happen?

1st floor hallway fire doors close    Y or N

2nd floor hallway fire doors close   Y or N

Gas cut off is automatic

* Core fan will run when water is flowed on these 2 risers

Building 3

(Housing Unit 3)

Risers are located in the Housing Unit 3 Sprinkler Room (SP- 01)

6 – 4 inch wet systems

| Riser | Area Covered | System Type | Test /Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 3A | Wet | On Riser & JC-02 of Pod 3A |
| B | Pod 3B | Wet | On Riser & JC-02 of Pod 3B |
| C | Pod 3C | Wet | On Riser & JC-02 of Pod 3C |
| D | Pod 3D | Wet | On Riser & JC-02 of Pod 3D |
| E* | 1st Floor Corridor | Wet | On Riser |
| F* | 2nd Floor Corridor | Wet | On Riser |

Gas reset is automatic

Gas reset box is located in the HU 3 F.A.C.P. room (ME-01) on the 2nd floor in the visitation corridor. Alarm panel (NODE 3) is located in the same room.

While flow testing risers E and F, did each of the following happen?

1st floor hallway fire doors close    Y or N

2nd floor hallway fire doors close   Y or N

Gas cut off is automatic

* Core fan will run when water is flowed on these 2 risers

Building 4

(Housing Unit 4)

Risers are located in the Housing Unit 4 Sprinkler Room (SP- 01)

6 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 4A | Wet | On Riser & JC-02 of Pod 4A |
| B | Pod 4B | Wet | On Riser & JC-02 of Pod 4B |
| C | Pod 4C | Wet | On Riser & JC-02 of Pod 4C |
| D | Pod 4D | Wet | On Riser & JC-02 of Pod 4D |
| E* | 1st Floor Corridor | Wet | On Riser |
| F* | 2nd Floor Corridor | Wet | On Riser |

Gas reset is automatic

Gas reset box is located in the HU 4 F.A.C.P. room (ME-01) on the 2nd floor in the visitation corridor. Alarm panel (NODE 4) is located in the same room.

While flow testing risers E and F, did each of the following happen?

1st floor hallway fire doors close    Y or N

2nd floor hallway fire doors close   Y or N

Gas cut off is automatic

* Core fan will run when water is flowed on these 2 risers

Building 5

(Housing Unit 5)

Risers are located in the Housing Unit 5 Sprinkler Room (SP- 01)

6 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 5A | Wet | On Riser & JC-02 of Pod 5A |
| B | Pod 5B | Wet | On Riser & JC-02 of Pod 5B |
| C | Pod 5C | Wet | On Riser & JC-02 of Pod 5C |
| D | Pod 5D | Wet | On Riser & JC-02 of Pod 5D |
| E* | 1st Floor Corridor | Wet | On Riser |
| F* | 2nd Floor Corridor | Wet | On Riser |

Gas reset is automatic

Gas reset box is located in the HU 5 F.A.C.P. room (ME-01) on the 2nd floor in the visitation corridor. Alarm panel (NODE 5) is located in the same room

While flow testing risers E and F, did each of the following happen?

1st floor hallway fire doors close    Y or N

2nd floor hallway fire doors close   Y or N

Gas cut off is automatic

* Core fan will run when water is flowed on these 2 risers

Building 6

(Housing Unit 6)

Risers are located in the Housing Unit 6 Sprinkler Room (SP- 01)

6 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 6A | Wet | On Riser & JC-02 of Pod 6A |
| B | Pod 6B | Wet | On Riser &J C-02 of Pod 6B |
| C | Pod 6C | Wet | On Riser & JC-02 of 6C Tower Hallway |
| D | Pod 6D | Wet | On Riser & JC-02 of Pod 6D |
| E* | 1st Floor Corridor | Wet | On Riser |
| F* | 2nd Floor Corridor | Wet | On Riser |

Gas reset is automatic

Gas reset box is located in the HU 6 F.A.C.P. room (ME-01) on the 2nd floor in the visitation Corridor. Alarm panel (NODE 6) is located in the same room.

While flow testing risers E and F, did each of the following happen?

1st floor hallway fire doors close    Y or N

2nd floor hallway fire doors close   Y or N

Gas cut off is automatic

* Core fan will run when water is flowed on these 2 risers

Phone in ME-02   Ext 3721

Building 7

(Pods 7A, 7B and 7C)

There are three riser rooms for this building:

Corridor to booking from HU7 - (SP- 01) - Riser for 7A

Corridor in front of HU7 Office - (SP- 01) - Risers for 7B & 7C

2nd floor visitation corridor- (HE- 01) Risers “D” &” E”

1 – 4 inch wet system

2 – 4 inch wet system

1 – 4 inch wet system

1 – 2 inch wet system

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 7A | Wet - 4 inch | On Riser & JC-02 of Pod 7A |
| B | Pod 7B | Wet - 4 inch | On Riser & JC-02 of Pod 7B |
| C | Pod 7C | Wet - 4 inch | On Riser & ME-02 on 2nd Floor |
| D* | 2nd Floor Corridor | Wet - 2 inch | On Riser & ME-02 on 2nd Floor |
| E* | 1st Floor Corridor | Wet - 4 inch | JC-01 next to pod 7A 1st Floor |

Gas reset is automatic

Gas reset box is on second floor inside (ME-01) Grey doors F.A.C.P. room. Alarm panel (NODE 7) is located in the same room.

Notes:

Large fire doors 2, 3 and 4 will lower when water flows on risers D and E. 2nd floor VC-01, VC-03 and VC-04 doors should close as well

*This test that is on the second floor

Roof Access to check fans:  - Hatch padlocks are SKD 11

Pod 7A -   HU7 2nd Floor (ME-01) FACP Room

Pod 7B & 7C - HU7     2nd Floor (ME-02) Room

***CORE fan is by the 7B roof hatch***

Building 8

(Pod 7D, Clinic and South Command)

Risers are located in South Command (SP- 01)

4 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 7D | Wet | On Riser & JC-01 & WH - 02 of Pod 7D |
| B* | Clinic | Wet | On Riser |
| C* | 1st Floor Corridor | Wet | On Riser |
| D* | 2nd Floor Corridor | Wet | On Riser |

Gas reset is automatic

Gas reset box is on second floor by 7-D (ME-01) Blue Doors (F.A.C.P.room).and is automatic.  Alarm panel (NODE 8) is located in the same room.

*While flow testing risers B, C and D, Fire door #1 will lower when water flows on these risers. 2nd floor VC-01 doors should close as well

2nd floor hallway fire doors close   Y or N

Notes:

Roof Access to check fans:  - Hatch padlock is a SKD 11

8 - 7 Delta & Clinic - Bld 8 2nd Floor (ME-01) FACP Room

AUX test drain also located within 7D Water Heater room on 2nd floor in pod – Flows for Riser “A”

7D has 2 smoke removal fans (One large for pod and one smaller unit for the wards

Office CP-01 in clinic is an SKD-02 key

Building 9:

(Employee Entrance/Gym/Roll Call Room)

Risers are located in the staff entrance area by Classroom “A” in (SP- 01)

1 – 2 ½ inch wet system

2 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Roll Call Room | Wet | On Riser |
| B | Gym/Locker Rooms | Wet | On Riser |
| C* | 2nd Floor | Wet | In Room |

Gas reset is automatic

Reset for hot water gas is upstairs. Access thru Classroom “A” then (ST-01)

Alarm panel (NODE 9) is located in the same room.

Notes:

*Butterfly and test valve are upstairs in the F.A.C.P. room.

AUX Drain located in JC-01 in Men’s Locker Room

Building 10

(Central Booking, Transfer Waiting, Records, Inmate Property, Sallyports)

Riser room located in releasing area (SP- 01)

6 - 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Booking/Records | Wet | JC in corner of fingerprint area |
| B | Records (Northside) | Wet | On Riser |
| C | Main Sallyport | Wet | Main Sallyport |
| D | Transfer Waiting | Wet | Transfer Waiting Sallyport |
| E | Property Room | Wet | JC-02 in property |
| F | FACP room | Wet | 2nd Floor FACP Room* |

*Test valve for riser “F” is behind air handler

Gas rest box is in (UA-01) 2nd floor of HU 7 blue double doors at the end of the hall in the  F.A.C.P. room Alarm panel (NODE 10) is located in the same room.

There are only 2 key stations in this area 1 in property room shower area and one in the booking clerk station.

There are also 2 butterfly valves by the entrance of UA-01 (Second Floor Tunnel) that are monitored and need to be exercised. Each one has a tamper switch.

Aux drains located in both sally ports and in the property room JC-01

Armory is an SKD-14

Courtroom is covered by this Node

Risers C & D converted from dry to wet Systems by Miken Fire on 01/2020

Building 10 (CBT/GPS):

Riser room is outside (EM-01) next to the GPS door

1-4 inch wet system

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| Single | CBT/GPS | Wet | * On Riser |

No gas reset associated with this area

Reports to NODE 10

*Need an 8 foot ladder to reach inspector’s test valve. There is a ladder stored within the riser room.

Building 11

(North Command)

Riser room located in North Command (SP-02)

2 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A* | 1st Floor Corridor | Wet | On Riser |
| B* | 2nd Floor Corridor | Wet | On Riser |

No gas reset associated with this area

Alarm panel (NODE 11) is located in 2nd Floor (ME-01) room by MCC

*Fire doors 2, 3 and 4 will lower when water flows on these risers

3 Smoke Evac fans activate on Bld. 11’s roof with water flow on all three risers.  Fans are marked AHU 42, 43 & 45.

Building 11

(Administration)

Riser room located in Admin Area (SP-01)

2 – 4 inch wet systems

1 – 1 inch wet system

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A* | Admin North - W | Wet | On Riser |
| B* | Admin South - E | Wet | On Riser |
| C* | Core Area | Wet | ME-01 on 2nd Floor |

*Fire doors 2, 3 and 4 will lower when water flows on these risers

Alarm panel (NODE 11) is located in 2nd Floor (ME-01) room by MCC

Notes:

ST-01 should release when water is flowed on riser “C”

May have to restart air handlers for admin area (in F.A.C.P. room) post testing.

**Test valve in F.A.C.P. room upstairs. Butterfly valve located in RD-01 and is in the ceiling – Need 6 ft ladder – One is located in the FACP room

Need an SKD 1 key to access former MCC - Need an SKD 9 key to access the IT area in former MCC.

3 Smoke Evac fans activate on Bld. 11’s roof with water flow on all three risers.  Fans are marked AHU 42, 43 & 45.

Building 12

(Kitchen and Tray Washing Area)

Riser room located in Kitchen Corridor (SP- 01) - Need Doorstop

5 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Staff Dining | Wet | On Riser |
| B | Kitchen | Wet | On Riser |
| C | Loading Dock/Dry Storage | Wet | On Riser |
| D | Tray Washing Area | Wet | On Riser |
| E* | Mechanical Room | Wet | 2nd Floor ME-01 - Tunnel |

Reset for hot water gas is on the second floor tunnel, inside the ME room to the right of the stairs leading to the 3rd floor. There is a light in the boiler room that will flash when gas is off. A green light will glow when gas is back on.

There is also a 2nd gas reset button is in kitchen office and the Boiler may have to be restarted

Alarm panel (NODE 12) is at the end of the 2nd floor tunnel, which is accessed thru Engineering (ST- 01)

* There is a butterfly valve in the ME-01 room at end of the Tunnel of Building 12 labeled as Riser “E” in the ceiling. Will need an 8 foot ladder to reach. The ladder is mounted at the end of the tunnel.

Aux drain located in tray prep area but it is capped

There is a control valve in the ceiling directly above the riser room door

8 Evac fans marked AHU’s 48, 49, & 50 are located in this area and will run with water flow

Dry Pendant heads are in the coolers.  All heads were replaced in June of 2013.

Building 13

(Engineering)

Riser room is located in Engineering (SP- 01)

4 – 4 inch wet systems

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | ECC | Wet | On Riser |
| B | Mech. Rooms | Wet | On Riser |
| C | 2nd Floor | Wet | On Riser |
| D | Fire Pump Room | Wet | On Riser |

No gas reset or evac fans associated with this area

Alarm panel (NODE 13) is located in former ECC

Building 14

(Warehouse)

Riser room is located in (EE- 01)

1 – 4 inch dry pipe system

| Riser | Area Covered | System Type | Test Valve Locations (2) |
| --- | --- | --- | --- |
| Single | Building 14 | Dry pipe | On Riser & in lawnmower shop on North side of building |

No gas reset associated with this area

Alarm panel (NODE 14) is located in (EE-01) room

There are 5 “drum drips” in warehouse

Riser valve must be reset by removing front cover (bolts are 15/16)

Inspector's test for dry pipe is located in lawnmower shop on the North side of the building

Clean pressure switch drain line each time you test

Dry Pendant heads are above the loading dock and coolers in Building 14. All heads were replaced in June of 2013.

Building 15

(Canteen/Engineer Warehouse)

No wet or dry fire suppression systems in this building