FALKENBURG ROAD JAIL

Wet Suppression System Testing Information

Updated 02/13/2020

68 Total Risers (only test 67 of them due to Bld. 13)

Quarterly Testing Requirements per NFPA 25

Inspect:

All FDC connections

All valves - Are in the appropriate open or closed position

Control Valves – Ensure they are locked, sealed or supervised

Gauges - Indicate that normal water pressure (50-60 PSI) is being maintained

Test:

Water flow alarms – Ensure signal is received by panel in MCC and horn strobes activate

Water flow bells - where installed - Should sound upon water flow

Supervisory switches on the Control Valves – Ensure signal is received by panel in MCC.

Main drains need to be exercised.

Ensure smoke fans work correctly in Housing Units 1, 3, 16 and 17.

Ensure gas mains shut down in Buildings 18 and 23

Annual Testing Requirements in addition to the above

Visual Inspection of all fire sprinkler heads

Fully open all main drains – Fully close all control valves

Open all AUX drains

Other Testing Notes

Sprinkler system gauges must be replaced or calibrated every 5 years

(NFPA 25-9-2.8.2)

System check valves must be inspected internally every 5 years

(NFPA 25 -9-4.2.1)

Dry sprinklers that have been in service for 10 years shall be replaced or tested. (NFPA 25- 5.3.1.1.1.6)

Dry Pendant heads are in the coolers/freezers of Buildings 18 and 22

Bld 18 installed - 2017

Bld 22 installed - 2016

BEFORE TESTING

Notify MCC

Ask them to make a general radio announcement that there will be fire systems testing.

Occupied areas

Notify the area supervisor that testing will be conducted

Tools you’ll need

Channel lock pliers

Ball valve handle

Spanner Wrench

A radio for the contractor to use

AFTER TESTING

Notify MCC

Ask them to make a general radio announcement that the fire systems testing has finished for the day.

Building 1

(Housing Unit 1)

Risers are located in the Housing Unit 1 Sprinkler Room (East ME room)

(System was converted from dry to wet by Miken fire on 04-07-15)

5 – 4 inch wet systems

10 pressure gauges – Replaced in 2015

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 1A | Wet | On Riser & ME-04 |
| B | Pod 1B | Wet | On Riser & ME-06 |
| C | Pod 1C | Wet | On Riser & ME-13 |
| D | Pod 1D | Wet | On Riser & ME-14 |
| Core | Core | Wet | On Riser - No AUX |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Did each second tier fan activate under water flow? |  |  |
| Are all up blast fans working? |  |  |
| Did the fireman’s panel in MCC display correctly? |  |  |

Notes

Smoke fans will activate in the respective pod individually upon water flow

2nd tier fans are normally “Off” and will activate under water flow

Water flow on the CORE riser will shut down FCU 1-1 (Office) only

(FCU -1-2 (tower) does not shut down because it is under 2000 CFM)

Will need an HVAC tech in MCC during testing and to conduct PM’s in HU-1.

1A – 31 monitor points on fireman’s panel

1B – 31 monitor points on fireman’s panel

1C – 31 monitor points on fireman’s panel

1D – 31 monitor points on fireman’s panel

Building 2

(Housing Unit 2)

Risers are located in the Housing Unit 2 Sprinkler Room (ME-01 East side)

2 – 4 inch wet systems

2 – 3 inch wet systems

6 pressure gauges* – Replaced in 2018

50-60 PSI normal pressure reading

*2 are in the ceiling of pods 2C and 2D

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 2A | Wet | On Riser -No AUX |
| B | Pod 2B | Wet | On Riser - No AUX |
| C | Pod 2C* | Wet | TL-01 ceiling of Pod 2C - No AUX |
| D | Pod 2D* | Wet | TL-01 ceiling of Pod 2D - No AUX |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

* The control valves for pods 2C and 2D are located in the respective ceiling hatch of   the TL-01 rooms in each pod

No water flow bell

Building 3

(Housing Unit 3)

(System was converted from dry to wet by Miken fire on 04-16-15)

Risers are located in the Housing Unit 3 Sprinkler Room (ME-13 East side)

5 – 4 inch wet systems

10 pressure gauges – Replaced in 2015

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test /Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 3A | Wet | On Riser & ME-01, 02, 03, 04 |
| B | Pod 3B | Wet | On Riser & ME-05, 06, 07, 08 |
| C | Pod 3C | Wet | On Riser & ME-09, 10, 11 ,12 |
| D | Pod 3D | Wet | On Riser & ME-14, 15, 16, 17 |
| E | Tower | Wet | Under North stairwell - No AUX |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon waterflow? |  |  |
| Did each second floor fan switch from Low to High? |  |  |
| Are all louvers working? |  |  |
| Did the fireman’s panel in MCC display correctly? |  |  |
| Did the four (4) large smoke fans work correctly? |  |  |

Notes

Smoke fans will activate in the respective pod upon water flow

2nd tier fans are normally “Off” and will activate under water flow

Will need an HVAC tech in MCC during testing and to conduct PM’s in HU-3.

3A – 24 monitor points on fireman’s panel

3B – 24 monitor points on fireman’s panel

3C – 24 monitor points on fireman’s panel

3D – 28 monitor points on fireman’s panel

No water flow bell

Building 4

(Housing Unit 4)

Risers are located in the Housing Unit 4 Sprinkler Room (ME-01 East side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 4A | Wet | On Riser & SR-01 of Pod 4A |
| B | Pod 4B | Wet | On Riser & SR-01 of Pod 4B |
| C | Pod 4C | Wet | On Riser & SR-01 of Pod 4C |
| D | Pod 4D | Wet | On Riser & SR-01 of Pod 4D |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

Building 5

(Housing Unit 5)

A and B Risers are located in the Housing Unit 5 Sprinkler Room (ME-01 West side)

C and D Risers are located in the Housing Unit 5 Sprinkler Room (ME-02 East side)

A & B

2 – 2 ½ inch wet systems

C & D

1– 4 inch wet system (Main)

2 – 2 ½ inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 5A | Wet | On West Riser - No AUX |
| B | Pod 5B | Wet | On West Riser - No AUX |
| C | Pod 5C | Wet | On East Riser - No AUX |
| D | Pod 5D | Wet | On East Riser - No AUX |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

No water flow bell on either side

No main drains on either riser

Building 6

(Housing Unit 6)

Risers are located in the Housing Unit 6 Sprinkler Room (ME-02 West side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 6A | Wet | On Riser & SR-01 of Pod 6A |
| B | Pod 6B | Wet | On Riser & SR-01 of Pod 6B |
| C | Pod 6C | Wet | On Riser & SR-01 of Pod 6C |
| D | Pod 6D | Wet | On Riser & SR-01 of Pod 6D |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

Building 7

(Housing Unit 7)

Risers are located in the Housing Unit 7 Sprinkler Room (ME-01 West side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 7A | Wet | On Riser & SR-01 of Pod 7A |
| B | Pod 7B | Wet | On Riser & SR-01 of Pod 7B |
| C | Pod 7C | Wet | On Riser & SR-01 of Pod 7C |
| D | Pod 7D | Wet | On Riser & SR-01 of Pod 7D |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

Building 8

(Housing Unit 8)

Risers are located in the Housing Unit 8 Sprinkler Room (ME-02 East side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 8A | Wet | On Riser & SR-01 of Pod 8A |
| B | Pod 8B | Wet | On Riser & SR-01 of Pod 8B |
| C | Pod 8C | Wet | On Riser & SR-01 of Pod 8C |
| D | Pod 8D | Wet | On Riser & SR-01 of Pod 8D |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

Will need a ball valve handle for the AUX drains in each pod

Alarms will sound in both 8A and 8B upon water flow in either pod

Alarms will sound in both 8C and 8D upon water flow in either pod

Building 9

(Housing Unit 9)

Risers are located in the Housing Unit 9 Sprinkler Room (ME-02 East side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 9A | Wet | On Riser & SR-01 of Pod 9A |
| B | Pod 9B | Wet | On Riser & SR-01 of Pod 9B |
| C | Pod 9C | Wet | On Riser & SR-01 of Pod 9C |
| D | Pod 9D | Wet | On Riser & SR-01 of Pod 9D |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon waterflow? |  |  |
| Did the waterflow bell activate? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

9B – Fresh air control switch is on a disconnect – Only one like this.

Building 10

(Housing Unit 10)

Risers are located in the Housing Unit 10 Sprinkler Room (ME-02 East side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 10A | Wet | On Riser & SR-01 of Pod 10A |
| B | Pod 10B | Wet | On Riser & SR-01 of Pod 10B |
| C | Pod 10C | Wet | On Riser & SR-01 of Pod 10C |
| D | Pod 10D | Wet | On Riser & SR-01 of Pod 10D |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

Will need a ball valve handle for the AUX drains in each pod

Alarms will sound in both 10A and 10B upon water flow in either pod

Alarms will sound in both 10C and 10D upon water flow in either pod

Building 11

(Housing Unit 11)

Risers are located in the Housing Unit 11 Sprinkler Room (ME-01 West side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 11A | Wet | On Riser & SR-01 of Pod 11A |
| B | Pod 11B | Wet | On Riser & SR-01 of Pod 11B |
| C | Pod 11C | Wet | On Riser & SR-01 of Pod 11C |
| D | Pod 11D | Wet | On Riser & SR-01 of Pod 11D |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

Building 12

(Housing Unit 12)

Risers are located in the Housing Unit 12 Sprinkler Room (ME-02 West side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 12A | Wet | On Riser & SR-01 of Pod 12A |
| B | Pod 12B | Wet | On Riser & SR-01 of Pod 12B |
| C | Pod 12C | Wet | On Riser & SR-01 of Pod 12C |
| D | Pod 12D | Wet | On Riser & SR-01 of Pod 12D |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Were all four fresh air fans tested? |  |  |

Notes

***Building 13***

***Belongs to Pet Resources***

***WE DO NOT TEST***

Riser is located in the Building 13 Sprinkler Room (ME West Side)

1 – 4 inch wet system

2 pressure gauges

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| Bld 13 | Bld 13 | Wet | On Riser - No AUX |

Building 14

(Support)

Risers are located in the East Outside Data Center area (Key to door is a 301)

2– 4 inch wet systems

1– 3 inch wet system

2 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| South | South Side Bld 14 | Wet | In front lobby ceiling* - No AUX |
| North | North Side Bld 14 | Wet | In electrical cage |
| North | North Side Bld 14 | Wet | In Supply Warehouse Ceiling (AUX drain)** |

|  | YES | NO |
| --- | --- | --- |
| Did all seven (7) AHU shut down upon water flow? |  |  |
| !!!No fresh air system in this building!!! | N/A | N/A |

Notes

No waterflow bell

*Will need a 8 ft ladder for the test valve in front lobby ceiling

**Will need a 6 ft ladder for the AUX drain in supply warehouse

Building 15

(Administration)

Riser is located in the West Double door ME room

1– 4 inch wet system

2 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| Bld 15 | Building 15 | Wet | On Riser |
| Bld 15 | Building 15 | Wet | In JD3 Suite in ceiling (AUX Drain) |

|  | YES | NO |
| --- | --- | --- |
| Did the AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| !!!No fresh air system in this building!!! | N/A | N/A |

Notes

* Will need an 8 ft ladder for AUX drain in the JD3 ceiling

Building 16

(Clinic A, Clinic B, JIC.JID)

Risers are located in the Building 16 Sprinkler Room (ME-02 East side)

4 – 4 inch wet systems

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pod 16A | Wet | On Riser & in Clinic A OF-14 then SR-01 |
| B | Pod 16B | Wet | On Riser & within dialysis room |
| C | Pod 16C | Wet | On Riser & within queuing area COM 2 room |
| D | Pod 16D | Wet | On Riser & within queuing area MG room |

|  | YES | NO |
| --- | --- | --- |
| Did each AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Did the smoke fans operate in JIC and JID? |  |  |
| Did the four (4) louvers operate? |  |  |
| Did the fireman’s panel in MCC display correctly? |  |  |

Notes

The FACP is located within the Clinic B vestibule

There is no smoke evacuation system in Clinic A and Clinic B

Water flow on the A riser will shut down both A & B AHU’s

Water flow on the B riser will shut down both A & B AHU’s

For JIC and JID, - The smoke evacuation system operates independently,

Upon water flow, smoke fans will operate and louvers will open in effected pod only.

8 monitor points of fireman’s panel

Will need HVAC tech to conduct PM’s in HU-16.

Building 17

(JIA and JIB)

Risers are located in the Building 17 Sprinkler Room (ME North side)

1 – 4 inch wet system

2 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| A | Pods 17A & 17B | Wet | On Riser & within JIA CH-07 |

|  | YES | NO |
| --- | --- | --- |
| Did the two (2) AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Did the smoke fans operate in JIA and JIB? |  |  |
| Did the eight (8) louvers operate? |  |  |
| Did the fireman’s panel in MCC display correctly? |  |  |

Notes

System has a singular flow switch.  Upon water flow, the smoke fans will operate and louvers will open in both pods. AHU's will shut down in unison as well.

12 monitor points of fireman’s panel.

Will need HVAC tech to conduct PM’s in HU-17.

Building 18

(Laundry and Kitchen)

Risers are located in the Building 17 Sprinkler Room (ME North side)

2 – 4 inch wet systems

2 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| Kitchen | Kitchen | Wet | On Riser & within DS-01 Ceiling |
| Laundry | Laundry | Wet | On Riser - No AUX |

|  | YES | NO |
| --- | --- | --- |
| Did the two (2) AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| Did the three (3) gas mains close? |  |  |
| Did you check the three (3) boiler resets? |  |  |
| !!!No fresh air system in this building!!! | N/A | N/A |

Notes

*Will need an 8 ft ladder for AUX drain in the kitchen DS-01 ceiling

Both AHU will shut down in unison upon water flow on either riser.

All 3 gas valves will also trip in unison upon water flow on either riser.

All three boiler reset buttons need to be pressed post testing

Large ovens DO NOT shut down under water flow or fire alarm activation.

All hood fans will shut down under an alarm condition

Ensure Water Heaters do not need to be reset.

Buildings 19 and 20

(Gatehouse and Shop)

No wet fire suppression systems in these buildings

Building 21

(Professional Visitation)

Riser is located in the Building 21 Sprinkler Room (ME South side)

1 – 3 inch wet system

2 pressure gauges – Replaced in 2015

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| Pro Visit | Pro Visit | Wet | On Riser - No AUX drain |

|  | YES | NO |
| --- | --- | --- |
| Did the AHU shut down upon water flow? |  |  |
| Did the water flow bell activate? |  |  |
| !!!No fresh air system in this building!!! | N/A | N/A |

Notes

Building Piggybacks off of the Building 14 FACP

Devices in Building 21 report as 14 -X -X on panel

Building 22

(Programs and Servery)

Risers are located in the East (ME-01) and West (ME-02) rooms

East Side (2 AHU)

2 – 4 inch wet systems

West Side (4 AHU)

1 – 4 inch wet system

4 pressure gauges – Replaced in 2018

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| East | North Prog-Court | Wet | On Riser – No AUX drain |
| East | South Programs | Wet | On Riser – No AUX drain |
| West | Vid Court- Servery | Wet | On Riser – No AUX drain |

|  | YES | NO |
| --- | --- | --- |
| Did the six (6) AHU shut down upon water flow? |  |  |
| Did the water flow bells activate? (One on each side) |  |  |
| !!!No fresh air system in this building!!! | N/A | N/A |

Notes

MAKE SURE VIDEO COURT IS NOT IN SESSION BEFORE TESTING

Water flow on any of the three risers will shut down all six (6) AHUs.

Devices in Building 22 report as 20 –X -X on panel

Building 23

(Central Energy Plant)

Riser is located in the Building 23 Chiller Room

1 – 3 inch wet system

2 pressure gauges – Replaced in 2016

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| CEP | Energy Plant | Wet | Northwest corner generator room - No AUX |

|  | YES | NO |
| --- | --- | --- |
| Did the water flow bell activate? (Bell is on the East outer wall) |  |  |
| Did the gas main close? |  |  |
| Did the generator bio-fuel shut down on both generators? |  |  |
| Did the COM-01 door release? |  |  |
| !!!No fresh air system in this building!!! | N/A | N/A |

Notes

Gas reset is on outside on the West wall of the building

Generator display screens - outline will go from yellow to red when bio-fuel shuts

down

COM-01 door is on the mezzanine

Devices in Building 23 report as 21 -X -X on panel

As of 3-26-18 - AHU 23-1 DOES NOT shut down under water flow

Building 24

(Inmate Vocational Training Building)

Riser is located in the Riser Room, southeast corner inside of the building.

1 –4 Inch wet system

2 Pressure gauges – New in 11-2019

50-60 PSI normal pressure reading

| Riser | Area Covered | System Type | Test/Aux Drain Location |
| --- | --- | --- | --- |
| 24 | Vocational Bld. | Wet | Northwest, inside, near “classroom area” |

|  | YES | NO |
| --- | --- | --- |
| Did the water flow bell activate? (Located on East outer wall) |  |  |
| Did the two (2) AHU’s shut down with water flow? |  |  |
| !!!No fresh air system in this building!!! | N/A | N/A |

Notes

Devices in Building 24 report as 13 -X -X on panel