ORJ Fire Alarm

Notes and Misc. 43

Contractor should test all panel batteries as part of the annual testing – If bad ones are discovered, they should be clearly marked and a work order to ISD should be submitted for replacement.

Smoke evacuation system – Someone needs to be on roof when these are activated to ensure that they are actually working.

Approximately 1,178 photo detectors total

CBT Area

There is a sub panel located in PD-01

Canteen building piggybacks off of Building 13

Heat Detectors in GEN room

Zip tie the heat gun to a Sherlock pole to test the high heats.

Duct detectors are supervisory non-latching – The air handlers ramp up when activated which is supposed to facilitate smoke evacuation. They do not shut down the AHU’s, At FRJ, they do shut down the AHU’s.

HU 1

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 1A | 36 | Dep Station |
| 1B | 36 (CC-17 has a different brand smoke) | Dep Station |
| 1C (Tower included) | 39 | Tower, Tower Hall(2nd fl), 1C Hall(1st fl) |
| 1D | 36 | Dep Station |
| 1st floor hall | 1 | At ST-02 |
| 1st floor under stairs | 2 (1 A & B side, 1 C & D side) | N/A |
| 2nd floor | 7 | At ST-02 |
| TOTALS | 157 | 8 |

There are no smoke detectors in the 1st floor “Learning Center”

5 duct detectors on the second floor in ME rooms (2 in ME-01, 3 in ME-02).

HU 2

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 2A | 36 | Dep Station |
| 2B | 36 | Dep Station |
| 2C* | 37 (1 is in vestibule ME room) | Dep Station |
| 2D | 36 | Dep Station |
| 1st floor hall | 1 | At ST-02 |
| 1st floor under stairs (EL) | 1 (A & B side) | N/A |
| 2nd floor | 7 | At ST-02 |
| TOTALS | 154 | 6 |

* This pod has one additional smoke detector because of the ME room in vestibule.

There are no smoke detectors in the 1st floor “Learning Center”

There is no smoke detector in SR-01 in the HU 2 1st floor hallway

There are no smoke detectors in the WH-01 & WH-02 rooms on the 2nd floor

There is no smoke detector in JC-01 room in the HU 2 2nd floor hallway

5 duct detectors on the second floor in ME rooms (3 in ME-01, 2 in ME-02).

HU 3

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 3A | 36 | Dep Station |
| 3B* | 37 (1 is in vestibule ME room) | Dep Station |
| 3C | 36 | Dep Station |
| 3D | 36 | Dep Station |
| 1st floor hall | 1 | At ST-01 |
| 1st floor under stairs (EL) | 1 (C & D side) | N/A |
| 2nd floor | 7 | At ST-02 |
| TOTALS | 154 | 6 |

* This pod has one additional smoke detector because of the ME room in vestibule.

There are no smoke detectors in the 1st floor “Learning Center”

There are no smoke detectors in the 1st floor “CL-01 Room”

There is no smoke detector in SR-01 in the HU 3 1st floor hallway

There are no smoke detectors in the WH-01 & WH-02 rooms on the 2nd floor

5 duct detectors on the second floor in ME rooms (3 in ME-01, 2 in ME-02).

HU 4

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 4A | 36 | Dep Station |
| 4B | 36 | Dep Station |
| 4C* | 37 (1 in in vestibule ME room) | Dep Station |
| 4D | 36 | Dep Station |
| 1st floor hall | 1 | At ST-01 |
| 1st floor under stairs (EL) | 1 (A & B side) | N/A |
| 2nd floor | 7 | At ST-02 |
| TOTALS | 154 | 6 |

* This pod has one additional smoke detector because of the ME room in vestibule.

There are no smoke detectors in the 1st floor “Learning Center”

There are no smoke detectors in the 1st floor “CL-01 Room”

There is no smoke detector in SR-01 in the HU 3 1st floor hallway

There are no smoke detectors in the WH-01 & WH-02 rooms on the 2nd floor

5 duct detectors on the second floor in ME rooms (3 in ME-01, 2 in ME-02).

HU 5

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 5A | 36 | Dep Station |
| 5B* | 37 (1 in vestibule ME room) | Dep Station |
| 5C | 36 | Dep Station |
| 5D | 36 | Dep Station |
| 1st floor hall | 1 | At ST-01 |
| 1st floor under stairs (EL) | 1 (C & D side) | N/A |
| 2nd floor | 7 | At ST-02 |
| TOTALS | 154 | 6 |

* This pod has one additional smoke detector because of the ME room in vestibule.

There are no smokes in the “Learning Center”

5 duct detectors on the second floor in ME rooms (3 in ME-01, 2 in ME-02).

HU 6

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 6A | 36 | Dep Station |
| 6B | 36 | Dep Station |
| 6C (Tower included) | 39 | Tower, Tower Hall(2nd fl), 6C Hall(1st fl) |
| 6D | 36 | Dep Station |
| 1st floor hall | 2 (1 A & B, 1 C & D side) | At ST-02 |
| 1st floor under stairs | 2 | N/A |
| 2nd floor | 7 | At ST-02 |
| TOTALS | 157 | 8 |

There are no smokes in the “Learning Center”

5 total duct detectors on the second floor in ME rooms (2 in ME-01, 3 in ME-02).

HU 7

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 7A | 36 | Dep Station |
| 7B | 36 | Dep Station |
| 7C (Tower included) | 22 | In Tower, in 7C Kitchen/Breakroom |
| 1st floor hall | 8 | Outside RE-01(LT Suite), At SV-03-01 Vestibule, Outside 7A |
| 2nd floor | 9 | At ST-7A, ST-7B, ST-7C |
| TOTALS | 111 | 10 |

4 total duct detectors on the second floor in ME rooms (1 in ME-01, 3 in ME-02).

Building 8

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 7D | 36 | End of HU-6 hall, Outside 7D in hall, Outside AT-39 |
| Clinic | N/A | In Clinic |
| 1st floor hall | 8 | N/A |
| 2nd floor | 8 | Where halls 4,5 & 6 meet, At ST-01 near 7D |
| TOTALS | 52 | 6 |

2 duct detectors on the second floor in the ME-01, 1 in ME-02.

Building 9

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| ME-01 | 2 | At Entrance, in Auditorium, In Gym, Outside Train Rm B |
| VD-01 | 1 |  |
| TOTALS | 3 | 3 |

6 total duct detectors on the second floor in the ME-01 room.

Building 10

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| Booking | 3 | 2 in Transfer Sallyport, Change-out hall, Records breakroom, Releasing hall/vestibule, Booking breakroom, behind Intake Class, 2 in Booking Sallyport |
| Tunnel | 4 |  |
| “Outside” ME Rooms, etc. | 6 |  |
| TOTALS | 13 | 9 |

4 total duct detectors, 1 in Records, 1 in SU-01, and 2 on the second floor.

Building 10 (CBT/GPS)

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| All | 7 | 2 in CBT at entrances, 1 in GPS by entrance. |
| TOTALS | 7 | 3 |

3 duct detectors in ceiling 1 in large office, 1 in open area, 1 in testing room).

Building 11

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 1st floor | 8 | Behind North Command, at SV-03-02, At SE-01(programs office), Front Lobby by entrance |
| 2nd floor | 9 | At ST-01, where halls 1,2 & 3 meet, across from ST-02-01, end of hall. |
| TOTALS | 17 | 8 |

6 total duct detectors, 2 first floor, and 4 on the second floor (1 in WH-01, 2 in ME-01, 1 in ME-02).

Building 12

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 1st floor | 1 | Room adjacent to dishwasher, Kitchen entrance, O.D. Room exit, hall vestibule |
| 2nd floor | 9 | In tunnel at ME-01 |
| TOTALS | 10 | 5 |

4 duct detectors on the second floor.

2 heat detectors in the Kitchen.

Building 13

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| 1st floor | 5 | Entrance, EG-01 south, EE-01 West |
| 2nd floor | 2 | In LR-01, CR-01, TN-01 |
| TOTALS | 7 | 6 |

2 heat detectors in generator room.

1 duct detector on the second floor.

3rd Floor “Tunnel”

| All Areas | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| All | 35 | At end of 1,2,3,4,5,6,7,8 & 11 |
| TOTALS | 35 | 9 |

All devices on 3rd floor report to node 13.

Building 14

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| EE-01 | 1 (25 feet high) | Mid roll-up door, back door |
| TOTALS | 1 | 2 |

4 total duct detectors, need a lift for one.

Heat detector in EE-01 (generator room).

Building 15 & 16

| AREA | TOTAL DETECTORS | PULL/KEY STATIONS |
| --- | --- | --- |
| Wood Shop (bld 15) | 2 | At both entrances (2) |
| Tool Room, Com, Welding, Lawn (bld 16) | 4 | At both Welding Shop entrances (2), Tool Room entrance, Com Room, Lawn Shop entrance |
| TOTALS | 6 | 7 |

Wood Shop reports to building 14.

Must reset to test each pull station in Wood Shop.

Rest of building 15 reports to building 13.

2 heat detectors in Welding, 2 in Lawn Shop (storage).