| HYDRANT NUMBER | Manufacturer | Year | GPM FLOW | SHUT OFF VALVE CHECKED | SHUT OFF DIRECTION | APPROXIMATE NUMBER OF TURNS TO CLOSE SHUT OFF VALVE | NOTES |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | American Darling | 2008 | 750 |  | Clockwise to close | 20 |  |
| 2 | American Darling | 2007 | 840 |  | Clockwise to close | 20 |  |
| 3 | US Pipe | 1997 | 840 |  | Clockwise to close | 21 |  |
| 4 | American Darling | 2001 | 920 |  | Counter clockwise to close | 17 | Outside fence |
| 5 | American Darling | 2007 | 840 | Need long T-handle | Clockwise to close | 20 |  |
| 6 | American Darling | 2001 | 920 | Need long T-handle | Counter clockwise to close | 18 |  |
| 7 | American Darling | 2001 | 1100 |  | Counter clockwise to close | 18 |  |
| 8 | American Darling | 2001 | 920 |  | Clockwise to close | 18 |  |
| 9 | American Darling | 2001 | 1000 |  | Counter clockwise to close | 18 |  |
| 10 | American Darling |  | 840 |  | Clockwise to close | 20 |  |
| 11 | American Darling | 2007 | 1000 |  | Clockwise to close | 20.5 |  |
| 12 | American Darling | 2001 | 920 | Need long T-handle | Counter clockwise to close | 19 | No stop point when opening / popping noise. |
| 13 | American Darling | 2008 | 920 | Need long T-handle | Counter clockwise to close | 18 |  |
| 14 | Mueller | 1997 | 840 |  | Clockwise to close | 20.5 |  |
| 15 | Mueller | 1997 | 840 | Need long T-handle | Clockwise to close | 20 |  |
| 16 | Mueller | 2015 | 920 | Need long T-handle | Clockwise to close | 19.5 | Outside fence |

Loop Valves (Loop valves connect the North and South Fire Mains to help ensure the facility maintains a Fire Water Supply)

Loop Valve 1 by Hydrant 14 SW of HU 5- 21.5 clockwise turns to close

Loop Valve 2 at SW corner of HU 10 - 26 clockwise turns to close

There are two shutoff valves (North and South) for the facility

Hydrants fed by South Main: 1, 2, 3, 14 & 15

(Valve by street - Counter clockwise to close)

Hydrants fed by North Main: 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 16

(Valve by street - Counter clockwise to close)

Building 1 Shutoff – Closes counterclockwise -  20.5 turns to close

Building 15 Shutoff – Closes clockwise -  26 turns to close

Building 21 Shutoff – Closes clockwise -  14.5 turns to close

Building 23 Shutoff – Closes counterclockwise - 31 turns to close

Building 24 Shutoff – Closes clockwise – 21 turns to close

Valve West side of HU 6 just before sidewalk – Closes counterclockwise - 31 turns to close - unknown as to function.

Valve in Dogrun – Counterclockwise to close – shuts off water to Buildings 4 and 15.

Valve on the West of HU 10 in Roadway - Closes clockwise - 38 turns to close – unknown as to function.

Valve in roadway between HU 11 and Bld 22 just before sidewalk - unknown as to function.

Valve on blacktop, east of Building 24 between forklift course racks and fence, shuts off fire hydrant #1 and Building 24 – Closes clockwise – 20.5 turns to close.