FRJ FIRE ALARM TESTING NOTES

UPDATED 10-22-19

Process will take about 7 days to complete properly

**MAKE SURE ALL FACP POWER SUPPLY BATTERIES ARE TESTED AND FACP PANELS RECEIVE  STICKERS FROM CONTRACTOR – Batteries are located in both East and West ME rooms on most buildings.

BRING WITH YOU:

LONG NEEDLENOSED PLIERS (BLD 16 ONLY)

SCREWDRIVER  BITS

NUT DRIVERS

SECURITY BIT SET

SMALL FLAT BLADE SCREWDRIVER

FIRE EXTINGUISHER TAGS AND PIN TIES

SPRAY LUBE

DUCT DETECTOR TESTERS

CAT 45 KEY

HATCH KEY(BLD 17 ONLY)

POLE DUSTER

CHANEL LOCK PLIERS

CLEAN RAGS

PVC SMOKE POLES

FLASHLIGHT

RADIO FOR SAM

CONTRACTOR NEEDS TO BRING:

LOTS OF CANNED SMOKE

LOTS OF CANNED AIR

BATTERY TESTER

PANEL INSPECTION TAGS

CAT 45 AND PULLSTATION KEYS

HEAT GUN AND EXTENSION CORD (BLD 18 ONLY)

**POST TESTING, Ensure ALL AHU units have returned to proper function and the system is unbypassed before you leave the area**

BUILDING 1

Duct detectors should shut down the AHU. They are “supervisory latching” - Panel will need to be reset to restart AHU.

They will not set off alarm but will activate smoke evac system.

Pull stations will set off the alarm and shut down the respective pod’s AHU and activate the smoke purge system.

Pod Smoke evacuation fans operate independently.

Rooftop exhaust fans have hinged panels that need to be lubricated – They will stick open if they are not.

There are 4 smaller smoke fans on the second floor of each mod (16 total) in the ME rooms – They also need to be checked for proper function.

EF1-1 EF1-2, EF1-3 and EF1-4 fans should shut down under waterflow, smoke detector and pullstation activation.

No smoke detector in riser room.

One smoke in tower and one in the FACP room.

2nd floor

2 smokes - 1 EL room and 1 DATA room (These do not activate the smoke fans).

Each pod has 3 duct detectors.

.

Core has single duct - does not activate smoke system, but should shut down the CFU

There is a pullstation at the North and South Entrance doors - They will set off the alarm in all four pods when activated.

HU 1

2nd Floor Mod Fans

These fans are normally "Off" and will only come on with alarm activation

| 2nd floor Mod Fans | FUNCTION Y/N | NOTES |
| --- | --- | --- |
| 1A MOD 1 |  |  |
| 1A MOD 2 |  |  |
| 1A MOD 3 | No fan | No fan in this mod |
| 1A MOD 4 |  |  |
| 1A MOD 5 |  |  |
| 1B MOD 1 |  |  |
| 1B MOD 2 |  |  |
| 1B MOD 3 |  |  |
| 1B MOD 4 | No fan | No fan in this mod |
| 1B MOD 5 |  |  |
| 1C MOD 1 |  |  |
| 1C MOD 2 |  |  |
| 1C MOD 3 | No fan | No fan in this mod |
| 1C MOD 4 |  |  |
| 1C MOD 5 |  |  |
| 1D MOD 1 |  |  |
| 1D MOD 2 |  |  |
| 1D MOD 3 |  |  |
| 1D MOD 4 | No fan | No fan in this mod |
| 1D MOD 5 |  |  |

BUILDING 2

ME rooms on roof – All four have 4 duct detectors- NO smokes or pulls.

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Pull stations will set off the alarm and shut down the respective pod’s AHU.

There is a smoke detector in the ductwork in pipechase CH-01 ONLY in all four pods

Will need a *6 foot ladder* to test these – Test when AHU is shut down.

All pod smokes are in the ceiling. Two are high and the other eight are lower (10 total) No smokes in the JC or SR rooms – Each pod only has 1 pull station.

The two pulls in the queuing area will activate the alarm in all four pods.

No smoke detector inside TELE room on the East side of building.

No smokes or pulls in the West ME room.

1 smoke and 1 pull in the East ME room.

*Pods 2C and 2D have control valves in the respective Deputy’s bathroom ceiling* only building like this.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 3

Activation of the singular pull station will activate the fire alarm in all four pods, but does not shut down the AHU’s or activate the smoke purge system.

Duct detectors are supervisory latching and will shut down the AHU. They will also activate the smoke evacuation system for the effected pod. The 6 ducts for the small core tower and office do not active the smoke purge.

14 total duct detectors on second floor (2 for each pod and 6 for CFU core tower/office).

Smoke detector activation will initiate smoke purge system for the respective pod in which the active device is located only.

There are 4 smaller smoke fans on the second floor of each mod (16 total) in the ME rooms – They also need to be checked for proper function. They are designed to run continuously and should be on “SLOW” - When the fire alarm is activated, they will switch to HIGH.

There are 44 duct servos on the second floor that need to be checked for proper function during the fire alarm testing;

3A = 8 + 2 high by main smoke fan

3B = 8 + 2 high by main smoke fan

3C = 8+ 2 high by main smoke fan

3D = 12+ 2 high by main smoke fan

When the smoke evac system is bypassed, it is normal for the small second floor fans to shut down once a smoke is activated.

HU 3 2nd Floor Mod Fans

| 2nd floor Mod Fans | FUNCTION Y/N | NOTES |
| --- | --- | --- |
| 3A MOD 1 |  |  |
| 3A MOD 2 |  |  |
| 3A MOD 3 |  |  |
| 3A MOD 4 |  |  |
| 3B MOD 1 |  |  |
| 3B MOD 2 |  |  |
| 3B MOD 3 |  |  |
| 3B MOD 4 |  |  |
| 3C MOD 1 |  |  |
| 3C MOD 2 |  |  |
| 3C MOD 3 |  |  |
| 3C MOD 4 |  |  |
| 3D MOD 1 |  |  |
| 3D MOD 2 |  |  |
| 3D MOD 3 | No fan | No fan in this mod |
| 3D MOD 4 |  |  |
| 3D MOD 5 | No fan | No fan in this mod |
| 3D MOD 6 |  |  |

BUILDING 4

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Pull stations will set off the alarm and shut down the respective pod’s AHU.

There are 2 pull stations (Vestibule and rec yard door) and 4 smokes in each pod (CH-01, CH-02, JC and SR).

There is 1 pull station, 2 smokes and 2 duct detectors in each pod's ME room on the roof.

There are 2 smokes in the Sgt Office – 1 in the DATA and 1 in the TELE rooms.

There is 1 smoke each in the SR and PN and 1 smoke in each respective TELE and DATA rooms.

The East and West ME rooms have 2 smokes and 1 pull station.

The ME rooms on the roof each have 2 smokes, 2 ducts and 1 pull station.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 5

ME rooms on roof – All four have 4 duct detectors- NO smokes or pulls.

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Pull stations will set off the alarm and shut down the respective pod’s AHU.

There is a smoke detector in the ductwork in pipechase CH-01 ONLY in all four pods

Will need a *6 foot ladder* to test these – Test when AHU is shut down.

All pod smokes are in the ceiling. Two are high and the other eight are lower (10 total) No smokes in the JC or SR rooms – Each pod only has 1 pull station.

The two pulls in the queuing area will activate the alarm in all four pods.

**No smoke detector inside TELE room on the East side of building**.

NO smokes or pulls in the West ME room.

1 smoke and 1 pull in the East ME room.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 6

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Pull stations will set off the alarm and shut down the respective pod’s AHU.

There are 2 pull stations (Vestibule and rec yard door) and 4 smokes in each pod (CH-01, CH-02, JC and SR).

There is 1 pull station, 2 smokes and 2 duct detectors in each pod's ME room on the roof.

There are 2 smokes in the Sgt Office – 1 in the DATA and 1 in the TELE rooms.

There is 1 smoke each in the SR and PN and 1 smoke in each respective TELE and DATA rooms.

The East and West ME rooms have 2 smokes and 1 pull station.

The ME rooms on the roof each have 2 smokes, 2 ducts and 1 pull station.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 7

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Pull stations will set off the alarm and shut down the respective pod’s AHU.

There are 2 pull stations (Vestibule and rec yard door) and 4 smokes in each pod (CH-01, CH-02, JC and SR).

There is 1 pull station, 2 smokes and 2 duct detectors in each pod's ME room on the roof.

There are 2 smokes in the Sgt Office – 1 in the DATA and 1 in the TELE rooms.

There is 1 smoke each in the SR and PN and 1 smoke in each respective TELE and DATA rooms.

The East and West ME rooms have 2 smokes and 1 pull station.

The ME rooms on the roof each have 2 smokes, 2 ducts and 1 pull station.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 8

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

No smokes in the PR or SR – None in DATA and TELE rooms.

1 smoke in office - Will sound alarm in all four pods.

A and B pods have 2 smoke detectors in each pipe chase, C and D pods have 1.

A & B pods have 22 total smoke detectors, C & D pods have 20.

WILL NEED a lift to test the six high smokes in each pod if you choose to do so.

Rooftop ME rooms

1 smoke.

2 ducts (Both supply).

No pulls.

West ME room (ground floor) – 1 smoke.

East ME room (ground floor) – 2 smokes.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 9

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Pull stations will set off the alarm and shut down the respective pod’s AHU.

There are 2 pull stations (Vestibule and rec yard door) and 4 smokes in each pod (CH-01, CH-02, JC and SR).

There is 1 pull station, 2 smokes and 2 duct detectors in each pod's ME room on the roof.

There are 2 smokes in the Sgt Office – 1 in the DATA and 1 in the TELE rooms.

There is 1 smoke each in the SR and PN and 1 smoke in each respective TELE and DATA rooms.

The East and West ME rooms have 2 smokes and 1 pull station.

The ME rooms on the roof each have 2 smokes, 2 ducts and 1 pull station.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 10

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

No smokes in the PR or SR – None in DATA and TELE rooms.

1 smoke in office - Will sound alarm in all four pods.

A & B pods have 2 smoke detectors in each pipe chase, C and D pods have 1.

A & B pods have 22 total smoke detectors, C & D pods have 20.

WILL NEED a lift to test the six high smokes in each pod if you choose to do so.

Rooftop ME rooms

1 smoke.

2 ducts (Both supply).

No pulls.

West ME room (ground floor) – 1 smoke.

East ME room (ground floor) – 2 smokes.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 11

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Pull stations will set off the alarm and shut down the respective pod’s AHU.

There are 2 pull stations (Vestibule and rec yard door) and 4 smokes in each pod (CH-01, CH-02, JC and SR).

There is 1 pull station, 2 smokes and 2 duct detectors in each pod's ME room on the roof.

There are 2 smokes in the Sgt Office – 1 in the DATA and 1 in the TELE rooms.

There is 1 smoke each in the SR and PN and 1 smoke in each respective TELE and DATA rooms.

The East and West ME rooms have 2 smokes and 1 pull station.

The ME rooms on the roof each have 2 smokes, 2 ducts and 1 pull station.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 12

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Pull stations will set off the alarm and shut down the respective pod’s AHU.

There are 2 pull stations (Vestibule and rec yard door) and 4 smokes in each pod (CH-01, CH-02, JC and SR).

There is 1 pull station, 2 smokes and 2 duct detectors in each pod's ME room on the roof.

There are 2 smokes in the Sgt Office – 1 in the DATA and 1 in the TELE rooms.

There is 1 smoke each in the SR and PN and 1 smoke in each respective TELE and DATA rooms.

The East and West ME rooms have 2 smokes and 1 pull station.

The ME rooms on the roof each have 2 smokes, 2 ducts and 1 pull station.

NOTES

Test fresh air fans for proper function via CEP.

BUILDING 14

Duct detectors should shut down the AHU. They will not set off alarm - Detectors for AHU 3 and AHU 5 are not located in the same room as the AHU - Look for the labels on the AHU's.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

2 smoke evac fan control boxes in ME-02 in transfer waiting hallway– fans cover the sallyport area. They are not connected to the fire alarm system.

Will need a 10 foot ladder to test the two ducts in the DMB Warehouse and the one within the Data Center.

FACP remote power supply and 6 and 8 foot ladders are located at the end of the transfer waiting hallway in ME-02.

1 pull inside Breadroom.

1 pull inside SCBA fill machine area.

2 smokes in mailroom.

BUILDING 15

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

No smoke evac fans.

BUILDING 16

Areas “CLINIC A” and “CLINIC B” do not have smoke evacuation systems, “JIC” and “JID” do.

JIC and JID have smokes in each pipe chase (12 in each pod).

Each pod has a non latching supervisory duct detector located above the cells FIA-01 (JIC) and FIB-20 (JID) – will need a 10 ft ladder to access hatches and crawlspace – Devices are located above the two high security single cells.

Each pod also has a keyed duct detector station with a remote test in the SR-02 of each pod. Will need a 6ft ladder or long needlenosed pliers to test.

2 ducts in JIC       (16-3-69 & 16-3-66)

2 ducts in JID        (16-3-67 & 16-3-70)

JIC and JID - 3 pulls each - Ensure pod smoke louvers open and close freely.

FACP is located in the Clinic B vestibule - Remote power supply located in the COM-02 room.

East and West ME room each have 2 smokes and 1 pull.

1 30ft high smoke in Clinic B.

Rooftop ME rooms

2 smokes.

2 ducts.

1 pull.

BUILDING 17

JIA and JIB each have a non latching supervisory duct detector located above the cells – will need a 10 ft ladder to check. Will also need the "HATCH” ECC 14 Key.

17-3-34 – JIA above cells

17-3-35 – JIB above cells

CH-07 in both JIA and JIB has 2 smokes within

Rooftop ME rooms - 2 ducts and 1 smoke within each.

Ensure pod smoke louvers open and close freely.

Duct detectors should shut down the AHU. They will not set off alarm

They are “supervisory latching” - Panel will need to be reset to restart AHU.

WILL NEED a lift to test the 4 high smokes in each pod if you choose to do so.

2 pulls in each pod.

2 Smokes in FACP room.

NOTES

Key-station 17-3-126 (Bld 17 queuing area) – Only shuts down AHU 17-2 (17B), AHU 17-1 (17A continues to run).

Key-station 17-3-127 (located within the Bld 17 Sgt’s Office) – Only shuts down AHU 17-1 (17A).  AHU 17-2 (17B continues to run).

BUILDING 18

Need a heat gun and extension cord.

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

Alarm activation will shut down hood fans at AHU’s.

Waterflow is only process that will shut down the gas valves.

No smoke evac fans.

2 heat detectors in boiler room will activate at 135 degrees.

2 heat detectors in ME-01 room will activate at 135 degrees.

Alarm activation WILL NOT shut down large ovens in kitchen, however, all hood exhaust fans will turn off.

Only 2 high smokes in the laundry.

Remote FACP power supply located in Data room within ME-01.

West ME -01 room device count

4 smokes, 2 heats, 4 ducts and 1 pull.

BUILDING 19

No suppression or alarm system

BUILDING 20

No suppression or alarm system

BUILDING 21

Duct detector should shut down the AHU. It will not set off alarm.

It is “supervisory latching” - Panel will need to be reset to restart AHU.

Device Count

5 pulls.

1 smoke.

1 duct.

BUILDING 22

***Alarm effects courtroom***

Duct detectors should shut down the AHU. They will not set off alarm.

They are “supervisory latching” - Panel will need to be reset to restart AHU.

WILL NEED a 6 foot ladder for the duct detectors in the East/West ME rooms.

No Smoke Evacuation Fans – Magnetic Doors should release when alarm is active.

OD Room- Must keep fewer than 50 chairs in this area to comply with exit rules.

BUILDING 23

Waterflow ONLY will shut off gas and biofuel controls to both generators (Display screen outlines will go from yellow to red) – mezzanine door will also release.

Device Count

9 smokes.

5 pullstations.

1 duct detector - Supervisory Latching - will shut down the AHU.

BUILDING 24

TBD

DEVICE COUNTS BY PHASE

Pods 2 and 5 (Phase 1)

There are 10 smoke detectors in each pod in the ceiling

None are inside the JC, SR or CH-01 and CH-02 rooms.

No smokes within rooftop ME rooms.

Pods 4, 6, 7, 9, 11 and 12 (Phase 2)

There are 4 smoke detectors in each pod (CH-01, CH-02, JC and SR rooms only, none in ceiling).

Each pod has 2 smoke detectors within the ME rooms on the roof as well.

Pods 8 and 10 (Phase 3)

A & B pods have 22 total smoke detectors.

C & D pods have 20 total smoke detectors.

(A & B pods have 2 smoke detectors in each pipe chase, C and D pods have 1).

Each pod has 1 smoke detector within the ME rooms on the roof as well.