Twice Yearly Halon Inspection per  NFPA 12A

1 system at ORJ only (OSC)

06-28-18

Disconnect solenoid from tank before performing any testing!

Twice a year, all systems shall be thoroughly
inspected, tested, and documented for proper operation by
trained competent personnel. (NFPA 12A 6.1.1)

Tanks are to be weighed annually as part of the testing (NFPA 12A 6.1.5)

*Will need an18” pipe wrench, 25' ft extension cord, 9/64 allen key and 9/16 deep socket.  Also need a portable scale to weigh the tank

OSC-Tank is in North Command corridor by housing unit one (ME-01)

232 lbs (Gas Weight)

409 lbs (Total Weight)

1 Pyrotronics CP2HR Control Panel

3 pull stations

3 abort buttons

(1 pull and 1 abort are located in SR-11 then in EE-02 behind monitors)

2 nozzles

(1 located in SR-12)

8 photo detectors (2 in SR -11 and 2 in SR -12)

1 bell

2 “Agent” lights

**Fire Alarm will sound at NODE 11**

Make sure all doors are closed in OSC. Is a violation if they are not!

“Three of the four large fire doors will lower when the Halon system is activated”

Historical HALON info

1 Charlie Tower – Halon tank was removed by VSC on June 1, 2010

6 Charlie Tower – Halon tank was removed by VSC on June 1, 2010

7 Charlie Tower – Halon system was removed in 2008

MCC – Wet sprinklers installed 05-02-13

ECC – Wet sprinklers installed 05-02-13