| HYDRANT NUMBER | Manufacturer | YEAR | GPM FLOW | Static Pressure | SHUT OFF VALVE CHECKED | SHUT OFF DIRECTION | APPROXIMATE NUMBER OF TURNS TO CLOSE SHUT OFF VALVE | NOTES |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | American Darling | 2008 | 1,025 | 70 |  | Counter clockwise to close | 20 |  |
| 2 | Mueller | 1988 | 1,190 | 68 |  | Clockwise to close | 18 |  |
| 3 | US Pipe | 2008 | 1,150 | 70 |  | Clockwise to close | 18 | Shut off valve is behind hydrant |
| 4 | Mueller | 1988 | 1,190 | 65 |  | Clockwise to close | 18 | Does not meet NFPA 24 7.3.3 (18' rule) – Needs a stainless plate |
| 5 | Mueller | 1988 | 1,100 | 70 |  | Clockwise to close | 19 |  |
| 6 | Mueller | 2009 | 1,150 | 71 |  | Clockwise to close | 19 | Valve is 10 feet down Need the 11.5 ft t-handle to operate |
| 7 | Mueller | 1988 | 1,190 | 70 |  | Clockwise to close | 18 |  |
| 8 | Mueller | 1988 | 1,190 | 70 |  | Clockwise to close | 18.5 |  |
| 9 | US Pipe | 1996 | 1,060 | 71 |  | Counter clockwise to close | 20 | Hydrant is located in front of the HREC |

Post Indicator Valve

Lone post indicator valve (PIV) by hydrant # 5 - replaced by Florida Fire 8-10-18 – closes clockwise – 31 Turns to close

Fire Main to Facility

On West side of HU 6 by Orient Road – Valves close counterclockwise – 22+ turns to close – Caps were painted red