FRJ Kitchen Hood Suppression Systems (NFPA 17) 9-3.1

Inspected and tested twice a year

07/11/19

Cleaning done 8/23/2018 by HCA

11.2.4* Fusible links (including fusible links on fire damper

assemblies) and automatic sprinkler heads shall be replaced at

least annually, or more frequently if necessary where required

by the manufacturer.

11.2.5 The year of manufacture and the date of installation of

the fusible links shall be marked on the system inspection tag.

The tag shall be signed or initialed by the installer.

Will need before testing:

12, 10 and 8 foot ladders (Available in the East ME Room)

GGM key for filter padlocks

"B363a" key for breaker panel

Allen key set

Flashlight

Long pilot light lighter

Spray lubricant for locks

Pushcart

Rags

The contractor will need a Buckeye keeper pin and reset tool

SPECIFICATIONS

System Installed – 5/17/17 by Florida Fire Service

Manufacturer – Buckeye “Kitchen Mister”

Six Agent Tanks

1 – 150 lb. tank (BFR 20)

1 – 107 lb. tank (BFR 15)

3 – 74 lb. tanks (BFR 10)

1 – 42 lb tank (BFR 5)

Pull-Stations - 4

Rooftop Fans - 6

Links

Hoods 1 and 2      Four (4) 360 degree

Hood 3                  Three (3) 450 degree

Hoods 4 and 5      Eight (8) 360 degree

Oven Hood           Four (4) 360 degree

HOODS 1&2

COVERS THE LARGE KETTLES

SYSTEM SPECIFICATIONS

One (1) 74 lb. tank (BFR 10)

One (1) 42lb tank (BFR 5)

Four (4) 360 degree links

Make sure the fans are switched “OFF" before testing

Pull the pullstation to test

DURING ACTIVATION;

The fire alarm will activate

AHU's 18-1 and 18-2 will both shut down

The main breaker in Panel “K” will trip

Rooftop hood fans 1 and 2 will run

On 12-31-18, hood fan 2 did not operate under Buckeye system activation – Osticket 050037

On 07-11-19, hood fan 2 did not operate under Buckeye system activation.

POST ACTIVATION;

MCC must “RESET” fire alarm post activation for AHU’s to restart.

The main breaker in Panel “K” on the East wall will need to be reset.

NOTES

Kettles are steam – No mechanical gas shut off valve on this system

Piper fire added a BFR 5 tank and a nozzle to hood 2 on 10-2-18 per Walbridge – This link is located in duct underneath the drip pan

HOOD 3

COVERS THE FRYER AND SKILLET

SYSTEM SPECIFICATIONS

One (1) 74 lb. tank (BFR 10)

Three (3) 450 degree links

Make sure the fan is switched “OFF" before testing

Pull the pullstation to test

DURING ACTIVATION;

The fire alarm will activate.

AHU's 18-1 and 18-2 will both shut down.

The main breaker in Panel “K” on the East wall will trip.

Manual gas shut off valve in ceiling will close (burners on range will die once valve trips)

Rooftop hood fan 3 will run.

POST ACTIVATION;

MCC must “RESET” fire alarm post activation for AHU’s to restart.

The main breaker in Panel “K” will need to be reset.

***MUST RE-IGNITE PILOT LIGHTS ON BURNERS***

NOTES

HOODS  4 & 5

COVERS THE TILT SKILLET AREA

SYSTEM SPECIFICATIONS

1 – 107 lb. tank (BFR 15)

1 – 150 lb. tank (BFR 20)

Eight (8) 360 degree links

Make sure the fans are switched “OFF" before testing

Pull the pullstation to test

DURING ACTIVATION;

The fire alarm will activate.

AHU's 18-1 and 18-2 will both shut down.

The main breaker in Panel “K” on the East wall will trip.

Manual gas shut off valve in ceiling will close (will have to remove junction box cover to observe)

Rooftop hood fans 4 and 5 will run.

POST ACTIVATION;

MCC must “RESET” fire alarm post activation for AHU’s to restart.

The main breaker in Panel “K” will need to be reset.

NOTES

OVEN HOOD

COVERS THE LARGE OVENS

SYSTEM SPECIFICATIONS

1 - 74 lb. tanks (BFR 10)

Four (4) 360 degree links

Pull the pullstation to test

DURING ACTIVATION;

The fire alarm will activate.

AHU's 18-1 and 18-2 will both shut down.

The main breaker in Panel “K” on the East wall will trip.

Manual gas shut off valve in ceiling will close (will have to remove junction box cover to observe)

The oven fan will run.

POST ACTIVATION;

MCC must “RESET” fire alarm post activation for AHU’s to restart.

The main breaker in Panel “K” will need to be reset.

NOTES