FE 25 Clean Agent Suppression System

12/19/2018

Building 14 Data Room -Key Set 369 “DAT” key

Call Todd Ryan or Rich Evans before doing any testing

ISD staff need to be on site

NFPA 2001

4-1.1 – System must be inspected and tested annually

4-1.3 – Gas must be weighed semi-annually

Installation Date – 08-19-2011

Installed by - United Fire

Manufacturer - Fike

Model – Xi-50 Cheetah (10-071)

Tank Size – 525 lbs

Detectors – 8    (4 are in the floor)

Nozzles –   4   (2 are visible, 1 is in the ceiling and 1 is under the floor)

*Need special solenoid reset tool post testing – This tool is stored inside the Cheetah panel*

**Must do a RESET on the Building 14 panel post testing

**